## Summary
Consumer + Storage Device Economic Model
Project Summary
NPV (₪) |  | Battery Capacity |  |  | Equity IRR (%) |  | Project IRR (%) | Average Annual Gross Yield (%) |  | Payback Period (Years)
3790987.3074 |  | 2280 |  |  | 65.71% |  | 23.38% | 22.2% |  | 3.9857
Seasonal Energy Consumption Patterns
Before Storage
| Total Consumption (kWh) |  |  | 6263338
| Total Annual Cost (₪) |  |  | 3220723.9848
|  |  |  | Consumption (kWh) | Cost (₪)
| Peak | Summer |  | 484210.12 | 693292.0498
|  | Winter |  | 276737.84 | 283102.8103
|  | Transitional Seasons |  | 373843.08 | 157687.0111
| Low | Summer |  | 1999715 | 895272.4055
|  | Winter |  | 1057466.72 | 408393.6473
|  | Transitional Seasons |  | 2071365.24 | 782976.0607
With Storage
| Total Consumption (kWh) |  |  | 6302803.6341
| Total Annual Cost (₪) |  |  | 2948624.8535
|  |  |  | Consumption (kWh) | Cost (₪)
| Peak | Summer |  | 304588.0802 | 436109.2132 | Description
|  | Winter |  | 101169.1731 | 103496.0641
|  | Transitional Seasons |  | 373843.08 | 157687.0111 | This chart illustrates the daily energy consumption during low and peak hours across different seasons: winter, summer, and transitional seasons. The histograms compare energy usage levels. The x-axis represents daily energy consumption in kilowatt-hours (kWh), while the y-axis indicates the frequency of days each consumption level is observed. This visualization aids in understanding the variations in energy consumption across seasons and time periods.
| Low | Summer |  | 2199295.0442 | 984624.3913
|  | Winter |  | 1252543.0165 | 483732.113
|  | Transitional Seasons |  | 2071365.24 | 782976.0607
Optimal Storage Size
[7 empty] | Description |  | Parameters
[7 empty] | his graph shows how the Project Internal Rate of Return (PIRR) changes with the size of the storage device (battery capacity). The x-axis represents the battery capacity in kilowatt-hours (kWh), and the y-axis shows the Project IRR.The optimal storage capacity, which maximizes the Project IRR, is kWh. |  | Global Constants | Exchange Rate (₪/$) | 3.7
[10 empty] | Inflation Rate | 6%
[10 empty] | Prime Interest Rate | 6%
[10 empty] | Discount Rate | 5%
[9 empty] | Financing Details | Marginal Annual Interest Rate | 0%
[10 empty] | Marginal Annual Interest Rate Growth | 0%
[10 empty] | Repayment Period (Years) | 0
[10 empty] | Own Funds Ratio | 0%
[10 empty] | Voltage Type | Low Voltage General Consumer IEC
[9 empty] | Capital Expenditure (Capex) | Initial Capex (₪) | 0
[10 empty] | Annual Opex (₪) | 0
[9 empty] | Additional Specifications | Response Time Window (hr) | <0.5
[10 empty] | Battery Cost per kWh ($) | 230
Optimal Use of Storage With Capacity of 2280 kWh
Description
Daily energy consumption during peak hours, comparing scenarios with and without a storage device. The orange line represents energy consumption without the storage device, while the green line illustrates consumption with the storage device. The graph is segmented into three seasons: winter, transitional seasons, and summer. Notably, during the transitional seasons, peak energy consumption is the same for both scenarios, reflecting zero arbitrage in these periods.
Description
This graph shows the percentage of battery usage by date, with the orange line indicating load shedding events in 2022 and the green line representing events in 2023. The transitional seasons are highlighted as the optimal times for participating in load shedding events, as battery usage is minimal during these periods.
Cash Flow
Description
This graph provides an overview of the annual cash flow for a storage project, detailing revenue sources and costs. The bars are color-coded: varying shades of green for revenues and red for costs, including operational expenses, loan repayments, and interest. The initial investment is highlighted at the start, and the net cash flow throughout the project’s lifespan is indicated by a black line.
Cummulative Cash Flow
Description
This graph shows the cumulative cash flow throughout the project’s lifespan. The point at which the investment is returned is marked during the 3rd year of the project, as indicated. The graph highlights how cash flow accumulates over time, providing a clear view of when the project breaks even and begins generating profit.

## Tabular Data
Economic Model For Storage Device
[8 empty] | Contact Information |  | גל זלוף
Parameters
|  | Global Constants | [9 empty] | Financing Details
|  | Exchange Rate (₪/$) |  |  |  | 3.7 | [5 empty] | Marginal Annual Interest Rate |  |  |  | 2%
|  | Inflation Rate |  |  |  | 6% | [5 empty] | Marginal Annual Interest Rate Growth
|  | Prime Interest Rate |  |  |  | 6% | [5 empty] | Repayment Period (Years) |  |  |  | 10
|  | Discount Rate |  |  |  | 5% | [5 empty] | Own Funds Ratio |  |  |  | 20%
[12 empty] | Voltage Type |  |  |  | Low Voltage General Consumer IEC
Additional Specifications
|  | Battery Cost per kWh ($) | [8 empty] | 230
|  | Response Time Window (hr) | [8 empty] | <0.5
|  | Battery Size (kWh) | [8 empty] | 2280
|  | Annual Degradation | [8 empty] | 2%
|  | Round-Trip-Efficiency | [8 empty] | 90%
|  | Depth-of-Discharge | [8 empty] | 100%
Capital Expenditure (Capex)
|  | Initial Capex (₪) | [8 empty] | 0
Annual Opex (₪)
Annual Consumption Data Summary
|  | Before Storage | [9 empty] | With Storage
|  | Total Consumption (kWh) |  | 6263338 | [7 empty] | Total Consumption (kWh) |  | 6302803.6341
|  | Total Annual Cost (₪) |  | 3220723.9848 | [7 empty] | Total Annual Cost (₪) |  | 2948624.8535
[6 empty] | Consumption (kWh) | Cost (₪) | [8 empty] | Consumption (kWh) | Cost (₪)
|  | Peak |  | Summer |  | 484210.12 | 693292.0498 |  |  |  |  | Peak |  | Summer |  | 304588.0802 | 436109.2132
|  |  |  | Winter |  | 276737.84 | 283102.8103 | שעות יקרות | [5 empty] | Winter |  | 101169.1731 | 103496.0641
|  |  |  | Transitional Seasons |  | 373843.08 | 157687.0111 | 1134081.8713 | 697292.2885 | -436789.5828 |  |  |  | Transitional Seasons |  | 373843.08 | 157687.0111 | 697292.2885
|  | Low |  | Summer |  | 1999715 | 895272.4055 |  |  |  |  | Low |  | Summer |  | 2199295.0442 | 984624.3913
|  |  |  | Winter |  | 1057466.72 | 408393.6473 | שעות זולות | [5 empty] | Winter |  | 1252543.0165 | 483732.113
|  |  |  | Transitional Seasons |  | 2071365.24 | 782976.0607 | 2086642.1135 | 2251332.565 | 164690.4515 |  |  |  | Transitional Seasons |  | 2071365.24 | 782976.0607 | 2251332.565
-272099.1313
Yearly Revenues Aggregation
[6 empty] | Total number of cycles per year |  | Battery Cost (₪) |  | Project Cost (₪) |  | Equity (₪)
[6 empty] | 176 |  | 1940280 |  | 1940280 |  | 388056
|  | חיסכון תעו״ז | מכירה
| Year | Revenue (₪) |  |  | Expenses |  |  |  |  | Project Cash Flow |  | Financing |  |  |  | Free Cash Flow |  | Gross Yield on Equity
|  | Load Shifting | Load Shedding | Total Revenue | Management Fees | Insurance | o&m | Unexpected Costs | Total Expenses | Per Year | Cumulative | fund | repayment | interest | total | per year | cumulative
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1940280 | -1940280 | 1552224 | 0 | 0 | 0 | -388056 | -388056 | 0%
| 1 | 272099.1313 | 251629.911 | 523729.0423 | 15711.8713 | 11400 | 0 | 3000 | 30111.8713 | 493617.171 | -1446662.829 | 1445074.7709 | 107149.2291 | 124177.92 | 231327.1491 | 262290.0219 | -125765.9781 | 25.44%
| 2 | 267342.5143 | 251629.911 | 518972.4253 | 15569.1728 | 11400 | 0 | 3000 | 29969.1728 | 489003.2525 | -957659.5765 | 1329353.6035 | 115721.1674 | 115605.9817 | 231327.1491 | 257676.1035 | 131910.1254 | 25.2%
| 3 | 262681.0296 | 251629.911 | 514310.9406 | 15429.3282 | 11400 | 0 | 3000 | 29829.3282 | 484481.6124 | -473177.9641 | 1204374.7428 | 124978.8608 | 106348.2883 | 231327.1491 | 253154.4633 | 385064.5887 | 24.97%
| 4 | 258112.7746 | 251629.911 | 509742.6856 | 15292.2806 | 11400 | 0 | 3000 | 29692.2806 | 480050.4051 | 6872.441 | 1069397.5731 | 134977.1696 | 96349.9794 | 231327.1491 | 248723.256 | 633787.8448 | 24.74%
| 5 | 253635.8848 | 251629.911 | 505265.7958 | 15157.9739 | 11400 | 0 | 3000 | 29557.9739 | 475707.8219 | 482580.2629 | 923622.2299 | 145775.3432 | 85551.8059 | 231327.1491 | 244380.6728 | 878168.5176 | 24.52%
| 6 | 249248.5327 | 251159.8169 | 500408.3496 | 15012.2505 | 11400 | 15960 | 3000 | 45372.2505 | 455036.0991 | 937616.362 | 766184.8592 | 157437.3707 | 73889.7784 | 231327.1491 | 223708.9501 | 1101877.4677 | 23.45%
| 7 | 244948.9277 | 246136.6206 | 491085.5483 | 14732.5664 | 11400 | 15960 | 3000 | 45092.5664 | 445992.9818 | 1383609.3439 | 596152.4989 | 170032.3603 | 61294.7887 | 231327.1491 | 214665.8327 | 1316543.3004 | 22.99%
| 8 | 240719.2285 | 241213.8882 | 481933.1167 | 14457.9935 | 11400 | 15960 | 3000 | 44817.9935 | 437115.1232 | 1820724.467 | 412517.5498 | 183634.9491 | 47692.1999 | 231327.1491 | 205787.9741 | 1522331.2745 | 22.53%
| 9 | 236567.5843 | 236389.6104 | 472957.1947 | 14188.7158 | 11400 | 15960 | 3000 | 44548.7158 | 428408.4789 | 2249132.9459 | 214191.8047 | 198325.7451 | 33001.404 | 231327.1491 | 197081.3298 | 1719412.6043 | 22.08%
| 10 | 232484.5415 | 231661.8182 | 464146.3597 | 13924.3908 | 11400 | 15960 | 3000 | 44284.3908 | 419861.9689 | 2668994.9148 | 1.6298e-09 | 214191.8047 | 17135.3444 | 231327.1491 | 188534.8199 | 1907947.4242 | 21.64%
| 11 | 228463.6022 | 227028.5818 | 455492.184 | 13664.7655 | 11400 | 15960 | 3000 | 44024.7655 | 411467.4185 | 3080462.3333 | 0 | 0 | 0 | 0 | 411467.4185 | 2319414.8427 | 21.21%
| 12 | 224521.3814 | 222488.0102 | 447009.3915 | 13410.2817 | 11400 | 15960 | 3000 | 43770.2817 | 403239.1098 | 3483701.4431 | 0 | 0 | 0 | 0 | 403239.1098 | 2722653.9525 | 20.78%
| 13 | 220619.1772 | 218038.25 | 438657.4272 | 13159.7228 | 11400 | 15960 | 3000 | 43519.7228 | 395137.7044 | 3878839.1475 | 0 | 0 | 0 | 0 | 395137.7044 | 3117791.6569 | 20.36%
| 14 | 216767.7212 | 213677.485 | 430445.2062 | 12913.3562 | 11400 | 15960 | 3000 | 43273.3562 | 387171.8501 | 4266010.9976 | 0 | 0 | 0 | 0 | 387171.8501 | 3504963.5069 | 19.95%
| 15 | 212950.9277 | 209403.9353 | 422354.863 | 12670.6459 | 11400 | 15960 | 3000 | 43030.6459 | 379324.2171 | 4645335.2147 | 0 | 0 | 0 | 0 | 379324.2171 | 3884287.7241 | 19.55%
| 16 | 209188.7689 | 205215.8566 | 414404.6255 | 12432.1388 | 11400 | 15960 | 3000 | 42792.1388 | 371612.4867 | 5016947.7014 | 0 | 0 | 0 | 0 | 371612.4867 | 4255900.2108 | 19.15%
| 17 | 205463.0344 | 201111.5395 | 406574.5738 | 12197.2372 | 11400 | 15960 | 3000 | 42557.2372 | 364017.3366 | 5380965.038 | 0 | 0 | 0 | 0 | 364017.3366 | 4619917.5474 | 18.76%
18
19
20
21
22
23
24
25
Projectile Metrics
NPV (₪) | [10 empty] | 3790987.3074
Equity IRR (%) | [10 empty] | 65.71%
Project IRR (%) | [10 empty] | 23.38%
Average Annual Gross Yield (%) | [10 empty] | 22.2%
Payback Period (Years) | [10 empty] | 3.9857
enSights may allow the Customer to use its Production Calculator which is currently under development and should be considered as beta version. The Production Calculator shall be deemed an integral part of the Platform, however, it is provided “as is” with no warranties whatsoever notwithstanding anything to the contrary in this Agreement.
“Production Calculator” means Company’s assisting tool for the sizing of BESS deployment.